The Town of Washington Grove

P. O. Box 216

300 Grove Avenue

Washington Grove, MD 20880

voice: 301-926-22566

email: washgrove@comcast.net

2024 Stormwater Infrastructure Maintenance

REQUEST FOR PROPOSAL

Bid Due Date:  June 7, 4:30 PM

PURPOSE: The Town of Washington Grove (“Town”) is currently experiencing issues related to how storm water with increasing volume and velocity is conveyed through the Town’s existing culvert and swale stormwater infrastructure designed to outdated standards and which has either filled in or collapsed.  It is the goal of this project to improve this conveyance system to mitigate stormwater damage in Town and its downstream impacts to the West Woods, and to achieve the maximum improvement in stormwater resilience to at least the 100-year storm event level. For reference, please see the Soltesz SWM Assessment Report: October 2023. This Request for Design/Build Proposals (RFP) seeks sealed bids from responsible contractors (“Contractor”) for maintenance and improvement of the existing storm water conveyance system within the public right of way in certain portions of the Town as specified in the project description, scope of work, and other contract documents.

- PROJECT DESCRIPTION:  The scope of work includes overall planning, design and construction to best manage the identified flows by renovating and improving existing swales, upgrading certain swale areas to bioswales, repairing or replacing specified culverts, and installing natural facilities in the following possible Areas (see Attachment A for map):

Area 1:

Culvert and swale renovations in the intersection of Chestnut Road and Acorn Lane. including improvements in the conveyance of stormwater into and from the culverts, asphalt roadway removal and installation of an upstream water quality facility which would provide quality and quantity control. The facility would be landscaped to match the aesthetics of the area.

Area 2:

Area 2a: Renovation of existing swale and possible installation of some bioswale on Chestnut Avenue between Oak Street and Center Street.

Area 2b: Renovation of existing swale and possible installation of some to bioswale on Chestnut Avenue north of Center Street.

Area 3:

Area 3a: Culvert and sump repair at Hickory Road and Center Street

Area 3b: Culvert and sump repair at Hickory Road and Oak Street

Area 4:

Area 4a: Swale maintenance and possible upgrade to bioswale where feasible on the south side of Oak Street between Chestnut Road and Chestnut Avenue.

Area 4b Replacement of asphalt swale with natural swale and possibly also bioswale where feasible on the south side of Oak Street between Chestnut Avenue and Hickory Road

Area 5:

Area 5a: Swale maintenance and replacement of asphalt swale with natural swale and possibly also bioswale where feasible on the south side of Center Street between Chestnut Road and Chestnut Avenue.

Area 5b: Swale maintenance or upgrade to possible bioswale where feasible on the south side of Center Street between Chestnut Avenue and Hickory Street.

Area 6:

Installation of a water quality facility, possibly a submerged gravel wetland, where Center Street terminates at Washington Grove Lane. Include a five-foot-wide walkway.

Area 7:

Removal of existing asphalt swale and installation of a water quality facility extending approximately 100 feet from Chestnut Avenue towards Hickory Road. Include an adjacent 5’ walkway between Chestnut Avenue and Hickory Road.

Area 8:

Swale renovation and installation of a French drain collection system along the west side of Chestnut Road beginning at the existing asphalt driveway and draining into the culvert sump at Center Street.

Area 9:

Sump repair at the intersection of Chestnut Road and Center Street.

- INITIAL SITE VISIT:  Prospective bidders are required to schedule and conduct an initial site visit with a Town Representative to ensure understanding of the work required.   All Areas of the Scope of Work are depicted on the map provided in Attachment A.

- SCOPE OF WORK:

- SITE EVALUATION, SURVEY, AND DESIGN

- UTILITIES: Contact Miss Utility and, as warranted, other private utility services to mark all Utilities within the intended area of work.

- SURVEY and DESIGN: The Contractor will survey each area of work requested using best available data to determine the contributory flows and level of engineering required to manage stormwater conveyance at each site and provide a signed drawing of existing conditions, including utilities, as a basis for design. Permitting, except as required and issued by the Town, is not expected to be required to complete the swale and culvert maintenance and improvements.

  - CULVERTS REPLACEMENTS: Prepare a drawing detailing the culvert replacement and sump improvements at Chestnut Road and Acorn Lane intersection Culvert replacement will be consistent with the specifications on Attachment B.

  - CULVERT REPAIR: Analyze the flows and prepare drawings to indicate proposed repairs to the culverts at the intersections of Hickory/Center and Hickory/Oak. Should culvert replacement be proposed, include drawings and calculations that describe the proposed scope of work. See Attachment B.

  - SWALES AND BIOSWALES: Prepare plans showing the basic grading for the renovated swales and improved bioswale locations. These plans will detail any trees or root zones which would be impacted, and any required removal of trees. However, avoiding root damage and impact on trees is desirable. Bioswale replacements will be constructed to be consistent with the schematic on Attachment C. Provide calculations indicating inflows and outflows used for sizing (length, width and depth) as well as locations and discharge path for outflows.

  - ASPHALT SWALES AND SHOULDERS: Prepare plans showing extent of asphalt removal and replacement with natural or bioswales to reduce the quantity and velocity of flows along Oak and Center Streets and in the vicinity of the church parking.  Provide calculations used for sizing of each and resultant reduction in flows. See Attachment B.

  - WATER QUALITY FACILITIES: Prepare plans showing the extent and details of the facilities proposed in Areas 1, 6 and 7.Prov  ide calculations for sizing including inflows and outflows and resultant detention capacity of the facility under design conditions. Indicate integration with current stormwater system as well as planting plans and surface walkway treatments.  See Attachment C.

- REFINEMENT OF THE SCOPE OF WORK: An on-site walk-through will be required to review plans and drawings with the Town representative(s), after which the final Scope of Work will be confirmed.

- REVIEW: Plans will be reviewed by Town representative(s) and should convey the limit of your proposal and demonstrate to the Town your understanding of the project. Bidders will be invited to present their proposal to the Washington Grove Town Council.

- DESIGN STANDARDS

Work will be designed in conformance with the latest edition of the Maryland Stormwater Design Manual that outlines the Best Management Practices (BMPs) adopted by the state to manage stormwater flows.

- PERFORMANCE OF WORK

- The contractor will complete all work agreed to in 3A within six-months of contract award. Later completion will be considered if advantageous to the project.

- As-built drawings will be provided for Town records prior to project completion.

- A final walk through will be conducted with Town representative(s) upon completion of the work to review all “punch list” items and confirm satisfactory installation.

- REQUIREMENTS FOR BIDDING: All bids must meet the following requirements.

- The fully completed, signed, and dated Bid Proposal; and

- The two completed affidavits; and

- A list of at least three references (names, addresses, email addresses, and phone numbers) from customers for whom similar work has been completed; and

- Itemized costs and linear feet of swales should be provided for each of the Areas for repair and renovation of culverts, swales, installation of bioswales, and installation of natural retention facilities, including any design and survey costs, using the Work Plan Budget Table in the Bid Proposal Form below, or on a comparable form.

- MANDATORY SUBMITTAL: THE ATTACHED BID PROPOSAL FORM OR EQUIVALENT, REFERENCES LIST, AND AFFIDAVITS MUST BE COMPLETED AND RETURNED.

The Proposal Form must be received by 4:30 p.m., June 7, 2024. It should be delivered as follows:

1) Enclosed in a sealed envelope marked “2024 Stormwater Infrastructure Management” and submitted to Town Clerk Kathy Lehman, P.O. Box 216, Washington Grove, Maryland 20880, or hand delivered to the Town Office, 300 Grove Avenue, AND ALSO

2) Made available as an electronic document(s) either via a link for download or by email to washgrove@comcast.net.

The contractor shall be familiar with the Town’s specifications.

The ‘Non-Collusion Affidavit’, and the ‘Affidavit with Respect to Non-Conviction, Non-Suspension and False Pretenses’ must be submitted along with the Bid Proposal Form (See, attached affidavits).

- BID EVALUATION:

- Bidders will be required to review their proposal at a meeting of the Washington Grove Town Council, and should contact the Town Office (above) to schedule this review.

- Award of the Contract is anticipated on July 8th.

- The Town, through its Town Council, will select the winning proposal based on “best value” within the available budget.  The Town will evaluate each proposal and assign a score to make a final selection. The Town reserves the option to select all or just portions of a proposal. The scoring will be as follows:

| No | Criteria | Points |
| --- | --- | --- |
| 1 | Technical Approach - Responsiveness to the scope of work, indicating clear understanding of the objective of the assignment - Comprehensiveness, reflecting a sufficient level of detail and appropriateness of proposed activities, - Implementation plan and proposed timeline are realistic and reflect all proposed elements of activity. - Discussion of how the bio swale will be implemented within the public right of way | 50 |
| 2 | Capabilities and Past Performance - Evidence/past history statement of organizational, financial and technical capabilities and resources to implement this work - Description of previous successful past experience implementing similar activities, including a minimum of one reference letter. | 20 |
| 3 | Proposed Costs - Reasonableness of proposed budget based on scope of activities proposed. - Summary budget, detailed budget, and budget notes included. | 30 |
|  | Total | 100 |

The Town reserves the right to reject any and all proposals and to waive formalities as may promote the best interests of the Town. Upon award, the successful bidder is required to sign a contract in substantially the form included in this RFP within ten calendar days of the award.

- EFFECTIVE DATE: The accepted proposal will be effective on an agreed date upon receipt of notice to proceed.

- CHANGES:  The Town may at any time issue a written change order to make changes within the general scope of the Contract in the work and services to be performed.  Any claim for an adjustment in time or money for a change order must be made in writing within 21 days from the date the Town issued the change order unless the Town extends this time period in writing.  Contractor must proceed with the prosecution of the work as changed, even if there is an unresolved claim.  No charge for extra work, time or material will be allowed, except as provided in this section. Increase or decrease in the work shall result in a change in the contract price based on the unit prices in the Bid Proposal Form.

- INSURANCE:  Within ten calendar days of the execution of this Contract and prior to commencement of work, Contractor must obtain at Contractor’s own cost and expense and keep in force and effect during the entire term of engagement until termination of this Contract the following insurance: comprehensive general liability insurance, workers’ compensation insurance, and automobile liability insurance with limits of not less than those set forth below.

A. Comprehensive General Liability Insurance:

Combined single liability limit of $1,000,000 per occurrence and $2,000,000 aggregate.

B. Automobile Liability Coverage:

Combined single liability limit of $1,000,000 per occurrence and $2,000,000 aggregate.

C. Workers’ Compensation:

Bidder shall comply with the requirements of the State of Maryland for the provision of workers’ compensation insurance.  By submission of a proposal, bidder herby certifies that they are in compliance with applicable requirements.

D. All insurance shall include completed operations and contractual liability coverage. On each policy, except for the workers’ compensation, the Town of Washington Grove shall be named as an additional insured with an additional insured endorsement.

Provision of any insurance required herein does not relieve the bidder of any of the responsibilities or obligations assumed by the bidder in the engagement agreement, or for which bidder may be liable by law or otherwise.

Provision of such insurance is not intended in any way to waive the Town’s immunities or any damage limits applicable to municipal governments as provided by law. By submission of a proposal, bidder hereby certifies that it is in compliance with all applicable requirements.

- INDEMNIFICATION:  Contractor shall be responsible for any loss, personal injury, death, and any other damage that may be done or suffered by reason of the negligent or intentional act or omission or failure to perform any contractual obligations by Contractor, its agents, servants, employees, and sub-contractors.  Contractor must indemnify and save the Town and its officials and employees harmless from any loss, cost, damage, and other expenses, including attorney’s fees and litigation expenses, suffered, or incurred, due to intentional or negligent acts or omissions, or failure to perform any of its obligations on the part of the Contractor, its agents, servants, employees, or subcontractors.

- INDEPENDENT CONTRACTOR:  The Contractor shall perform the services described herein as an independent contractor and not as an employee of the Town.

- OTHER PAYMENTS; EXPENSES; TAXES:  The Town will not be responsible for any cost or expenses of operation of any kind associated with Contractor’s provision of services pursuant to this Contract, except as set out herein.  Contractor shall be entitled to no fees, bonuses, contingent payments, or any other amount in connection with the services to be rendered hereunder except as set out herein.  The parties hereto further agree that the Town shall have no obligation to reimburse, pay directly or otherwise satisfy any expenses of the Contractor in connection with the performance of Contractor’s obligations under this Contract, except as set out herein.  It is expressly understood and acknowledged by the parties hereto that the fees payable hereunder shall be paid in the gross amount, without reduction for any Federal or State withholding or other payroll taxes, or any other governmental taxes or charges.  The parties hereto further recognize that Contractor, as an independent Contractor of the Town, is responsible for directly assuming and remitting any applicable Federal or State withholding taxes, estimated tax payments, Social Security payments, unemployment compensation payments, and any other fees, taxes, and expenses whatsoever.  In the event that Contractor is deemed not to be an independent contractor by any local, state or federal governmental agency, Contractor agrees to indemnify and hold harmless the Town for any and all fees, costs and expenses, including, but not limited to, attorney’s fees incurred thereby.

- ASSIGNMENT AND TERMINATION:  The Contractor will not assign or transfer any interest or claim under this Contract except as authorized in writing by the Mayor of Washington Grove.

- TERMINATION FOR DEFAULT:  Notwithstanding anything to the contrary herein, this Contract may be terminated upon the failure of the Contractor to deliver work, supplies, materials, or services in a timely manner, to correct defective work or materials, to act in good faith, or to carry out the work in accordance with contract documents, each of which shall constitute a breach of this Contract.  In such event, the Town may give notice to the Contractor to cease work until the cause for such order has been eliminated.  Should the Contractor fail to correct such default within 24 hours after receipt of notification, the Town may terminate this Contract.  This provision shall not limit the Town in exercising any other rights or remedies it may have.

- TERMINATION FOR CONVENIENCE:  The performance of work or delivery of services under this Contract may be terminated in whole or in part at any time upon written notice when the Town determines that such termination is in its best interest.  The Town will be liable only for labor, materials, goods, and services furnished prior to the effective date of such termination.

- COMPLIANCE:  The Contractor will, without additional expense to the Town, be responsible for complying with any and all applicable laws, codes, and regulations in connection with the services called for in this Contract.

- PAYMENTS: Payments for the completed work shall be made on the basis of approved invoices.  All invoices will contain complete and accurate information.  Under no circumstances will the Town pay the Contractor for interest on amounts payable.  Invoices should be sent to the Town Clerk, Kathy Lehman, P.O. Box 216, Washington Grove, Maryland 20880.

Payment will be made within 30 days of the Town’s receipt of approved invoices.  No payment may be made under this Contract unless funds for the payment have been appropriated by the Town.

- TERM: The initial term of the contract is six-months from the Effective Date (or a later date if agreed to by the Town). Extension may be negotiated, but will only be granted if advantageous to Project completion.

- PROJECT INFORMATION CONTACTS: For further information, contact Town Clerk Kathy Lehman (301-926-2256).

ATTACHMENT A

Map showing Work Areas.

ATTACHMENT B

Culvert and Swale Repair or Replacement on Chestnut Road and Acorn Lane Intersection

Culverts need to be replaced and upsized at the intersection of Chestnut Road and Acorn Lane and the corresponding swale drainage improved.  The project will consist of three end walls and the replacement of the existing pipe with new 24” pipe, as well as replacement of pavement as needed to install the culvert.  As part of the installation of the culvert, pavement in the intersection will be reduced to create the required sump condition.

The contractor will need to provide the following:

- Class V RCP pipe.  The contractor will provide a submittal for review by the Town of Washington Grove.

- The Contractor Shall replace a pavement section to meet or exceed the requirements of Montgomery County Residential Road Standards.

- A 2” Mill and Overlay will be provided extending approximately 20’ from the edges of road disturbance.

- Design and install a stormwater quality facility upstream of the culvert sump to best manage flows into the culvert

Culvert and sump repair or replacement at Hickory Road and Center Street and Hickory Road and Oak Street intersections

Culverts, sumps and stormwater structures need to be inspected and recommendations made for clean out, repair and/or replacement. Verify sizing for the current and anticipated flows. If a redirection is recommended, provide an alternative design. If culvert replacement is recommended, follow the 4 points above.

Asphalt swale and shoulder replacement

Examine efficacy of replacing sections of asphalt with natural swales and/or section of bioswale for each designated area. Include cutting and removal and disposal of asphalt and any gravel base as well as soil removed. The Town may be able to use the soil. Stabilize remaining edge of asphalt. Calculate flows and detention capacity of recommended swale and/or bioswale. Follow guidelines for bioswale below.

ATTACHMENT C

Bioswale Renovation

The contractor will regrade the existing swales to reflect the detailed example below.  The swale may have a 2’ bottom width, a 9” minimum depth and will have sod placed on all disturbed areas of the project once the bio mix and gravel have been installed.

Water Quality Facilities

Analyze flows and design each facility to reduce the quantity and velocity of the individual flows. Calculate the detention capacity and proposed reduction in flow. Provide details of the facility and proposed surface treatment and plantings.  Incorporate a gravel pathway where indicated. Provide examples of similar constructed facilities.

Town of Washington Grove

Request for Proposals

Stormwater Infrastructure Management

BID PROPOSAL FORM (2 Pages)

Town of Washington Grove    			BID DUE DATE:  June 7, 2024

300 Grove Avenue; PO Box 216    				TIME:  Before 4:30 p.m.

Washington Grove, MD  20880

_____________________________________________________________________________

(Company)

hereby submits an attached Work Plan Budget and Timeline Proposal for 2024 Stormwater Infrastructure Maintenance within the Town of Washington Grove, Maryland.  Having carefully examined the Request for Proposals, Instructions to Bidders, the Plans and Specifications, the proposed Contract and Attachments A, B, and C, and having received clarification on all items of conflict or upon which any doubt arose, the undersigned proposes to furnish all labor, equipment, materials, etc., required by the documents, all in strict accordance with the contract documents, and to perform the design/build work described for Project in the submitted Work Plan Budget and Timeline Proposal.

Proposals should be itemized for each of the Areas in the Scope of Work and include at least the following information submitted in summary form and greater detail as appropriate on attachments.

WORK PLAN BUDGET

|  | Cost Category |  | Rate | Per Unit | Total (USD) | Notes: |
| --- | --- | --- | --- | --- | --- | --- |
| I. Engineering Survey and Design |  |  |  |  |  |  |
|  | (limited to staff providing direct service) |  |  |  |  |  |
|  | Area 1 |  |  |  |  |  |
|  | Area 2a |  |  |  |  |  |
|  | Area 2b |  |  |  |  |  |
|  | Area 3a |  |  |  |  |  |
|  | Area 3b |  |  |  |  |  |
|  | Area 4a |  |  |  |  |  |
|  | Area 4b |  |  |  |  |  |
|  | Area 5a |  |  |  |  |  |
|  | Area 5b |  |  |  |  |  |
|  | Area 6 |  |  |  |  |  |
|  | Area 7 |  |  |  |  |  |
|  | Area 8 |  |  |  |  |  |
|  | Area 9 |  |  |  |  |  |
|  | TOTAL Design Cost |  |  |  | $ - |  |
| II. Construction |  |  |  |  |  |  |
|  | Area 1 |  |  |  |  |  |
|  | Area 2a |  |  |  |  |  |
|  | Etc. |  |  |  |  |  |
|  | Etc. |  |  |  |  |  |
|  | TOTAL Construction Cost |  |  |  | $ - |  |
| III. Reimbursable Expenses |  |  |  |  |  |  |
|  | Area 1 |  |  |  |  |  |
|  | Area 2a |  |  |  |  |  |
|  | Etc. |  |  |  |  |  |
|  | Etc. |  |  |  |  |  |
|  | TOTAL Reimbursable Costs |  |  |  | $ - |  |
| VI. OTHER DIRECT COSTS |  |  |  |  |  |  |
|  | Area 1 |  |  |  |  |  |
|  | Area 2a |  |  |  |  |  |
|  | Etc. |  |  |  |  |  |
|  | Etc. |  |  |  |  |  |
|  | TOTAL Other Direct Costs |  |  |  | $ - |  |
|  | GRAND TOTAL |  |  |  | $ - |  |

WORK PLAN TIMELINE

The Contractor will provide products and services as required beginning immediately upon award of the contract to on or about August 1, 2024, or a later negotiated date, for the fixed rates established in the Budget

| Activity | Aug | Sept | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Engineering Survey and Design |  |  |  |  |  |  |  |  |  |  |
| Town Review and Confirmation |  |  |  |  |  |  |  |  |  |  |
| Construction |  |  |  |  |  |  |  |  |  |  |
| As-built Drawings |  |  |  |  |  |  |  |  |  |  |
| Close out and Punchlist |  |  |  |  |  |  |  |  |  |  |

Name of Bidder:

________________________________________________________________

Name of Individual Authorized to Bind the Bidder:

_____________________________________

Signature:

__________________________________________________________________

Federal Tax ID Number: ___________________________

Date: ________________________________________

SPECIAL TERMS AND CONDITIONS:

A.  Failure to fill in all blanks properly and completely may be cause for rejection of this proposal.

B.  It is understood that the proposal price will be firm for a period of sixty (60) calendar days from the proposal opening date, and that, if the undersigned is notified of award of contract within this time period, the Bidder shall execute a contract for the above stated compensation.

C. The bid prices shall be stated in both words and figures.

TO BE SUBMITTED WITH BID

Non-Collusion Affidavit

___________________________________, being duly sworn on oath, deposes and says:

That he/she is the

______________________________________________________________________

(Owner, Partner, Title if on behalf of a Corporation)

of ___________________________________________________________________,

(Name of Business, Corporation or Partnership)

the party submitting the foregoing Bid; that (he has not) (no officer of the said Corporation has) (no partner of the said Partnership has) nor has any person, firm or corporation acting on (his/her) (its) (their) behalf; agreed, conspired, connived or colluded to produce a deceptive show of competition in the compilation of the Bid being submitted herewith; and that (he/she) (the said Corporation) (the said Partnership) has not in any manner, directly or indirectly, entered into any agreement, participated in any collusion to fix the Bid Price of the Bidder herein or any competitor, or otherwise taken any action in restraint of free competitive bidding in connection with the contract for which the within Bid is submitted; that in making this Affidavit, the affiant represents that he/she has personal knowledge of the matters and facts herein stated.  The Affiant hereby declares and affirms under the penalties of perjury that the foregoing is true to the best of his/her knowledge and information.

____________________________(SEAL)

To be signed by Bidder, if the Bidder is an Individual; or by a Partner, if the Bidder is a Partnership; or by a duly authorized Officer, if the Bidder is a corporation.

TO BE SUBMITTED WITH BID

AFFIDAVIT WITH RESPECT TO NON-CONVICTION, NON-SUSPENSION AND FALSE PRETENSES

I hereby affirm that:

- I am the ___________________________ (Title) and duly authorized representative of

______________________________ (Name of Business Entity) whose address is

________________________________ and that I possess the legal authority to make this affidavit on behalf of myself and the firm for which I am acting.

- Except as described in Paragraph 7 below, neither I nor the Business Entity nor, to the best of my knowledge, any of its officers, directors, or partners or any of its employees directly involved in obtaining contracts with the State, or any county, bi-county or multi-county agency or subdivision of the State have been convicted, or in an official investigation or other proceeding admitted in writing or under oath, acts or omissions which constitute bribery, attempted bribery or conspiracy to bribe under the provisions of Criminal Law Article of the Annotated Code of Maryland or under the laws of any state or the federal government (conduct prior to July 1, 1977 is not required to be reported); and

- Except as described in Paragraph 7 below, neither I nor the Business Entity nor, to the best of my knowledge, any of its officers, directors, or partners or any of its employees directly involved in obtaining contracts with the State, or any county, bi-county or multi-county agency or subdivision of the State have been convicted under a State of federal law or statute of any offense enumerated in §16-203 of the State Finance and Procurement Article; and

- Except as described in Paragraph 7 below, neither I nor the Business Entity nor, to the best of my knowledge, any of its officers, directors, or partners or any of its employees directly involved in obtaining contracts with the State, or any county, bi-county or multi-county agency or subdivision of the State have been found civilly liable under a State or federal antitrust statute as provided in §16-203 of the State Finance and Procurement Article.

- Except as described in Paragraph 7 below, neither I nor the Business Entity nor, to the best of my knowledge, any of its officers, directors, or partners or any of its employees who will provide, directly or indirectly, supplies, services, architectural services, construction related services, leases of real property, or construction have been debarred or suspended under this subtitle.

- Except as described in Paragraph 7 below, neither I nor the Business Entity nor, to the best of my knowledge, information and belief, any officer, director, partner, member or associate thereof; nor any of its employees directly involved in obtaining contracts with the Town, has been convicted of false pretenses, attempted false pretenses or conspiracy to commit false pretenses under the laws of any state or federal government, based upon acts committed after July 1, 1981.

- State “none” below or, as appropriate, list any suspension, debarment, conviction, plea, or admission described in Paragraph 2 - 6 above, with the circumstances, date, court, official or administrative body, the individuals involved and their position with the firm, and the sentence or disposition, if any.

I acknowledge that this affidavit is to be furnished, where appropriate, to the Town of Washington Grove, Maryland, under Section 16-311 of the State of Maryland Finance and Procurement Article of the Annotated Code of Maryland.  I acknowledge that, if the representations set forth in this affidavit are not true and correct, the Town of Washington Grove may terminate any contract awarded and take any other appropriate actions.  I further acknowledge that I am executing this affidavit in compliance with Section 16-309 of the State Finance and Procurement Article of the Annotated Code of Maryland, which ordains that any person convicted of bribery (upon acts committed after July 1, 1977) in furtherance of obtaining a contract from the State or any subdivision of the State of Maryland shall be disqualified from entering into a contract with the Town.

I do solemnly declare and affirm under the penalties of perjury that the contents of the affidavit are true and correct.

_______________________

Date

________________________________________________________

Signature

__________________________________________

Printed Name